## Introduction
Qualification Report Template for: |  |  | Tesla M40 PCIe
Instructions: | This template is intended to be used by OEM/ODM/system integrators for NVIDIA product qualification.
This report should be populated in full and then submitted to NVIDIA for review and approval.
ALL DATA REQUIRED FROM THE CUSTOMER IS HIGHLIGHTED IN YELLOW CELLS
Date: | 2018-05-21
Contents: | This template contains the following worksheets:
Thermal Map & Qual worksheet
Power Qual worksheet
Mechanical worksheet
SMBus worksheet
PCI Express Qual worksheet
Stress Test worksheet
GPU Direct worksheet
Input EDPp worksheet
Scope: | This template is intended for a single chassis configuration. The chassis should have all NVIDIA boards installed and operating during the qualification run.
Note: | Before running NVQual, OEMs need to disable any system or Intel's power management features (such as EIST) to prevent them from interfering with NVQual
CUSTOMER DATA
Model | 3U8G+/C621
Photos: | Please attach photos of the following:
- All board locations in chassis, indicating each board location and chassis air inlet location.
- For thermal qualification, indicate airflow inlet to the worst-case board location, heat sink inlet temperature measurement location, and airflow measurement location
- Chassis placement in cabinet or rack (if applicable), indicating worst-case chassis location for thermal qualification, and airflow direction.
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## Power
Power Qualification |  |  |  | Tesla M40 PCIe
IMPORTANT
- Record the following data with all graphics boards populated in a single chassis (rack/blade). The system loading should match the production configuration.
- Customers are required to run the NVQual Thermal Qual at their Worst Case Ambient temperature.
- The NVQual Thermal Qual will be executed on all graphics boards in the chassis. The GPU Tj and Average Input Power is reported in the MODS log file
- Only the worst case GPU Temperature (Tj) and Input Power reported should be captured in the table below.
|  | Temperature |  |  |  | Input Voltage |  | Tolerance |  | Voltage |  | Voltage |  | Comments
| NVQual Thermal Qual at Worst Case Ambient Temperature | GPU Tj | Input Power | Ambient | Inlet | Voltage Rail | Description | Min | Max | Min | Max | Min | Max
|  | 76 deg C | 42 deg C | 35 deg C | 37 deg C | 3V3 | PCIe | -8% | 8% | 3.036 | 3.564 | 3.33 V | 3.55 V
[6 empty] | 12V | PCIe | -8% | 8% | 11.04 | 12.96 | 11.7 V | 12.7 V
[6 empty] | 12V | ESP12 8-pin | -8% | 8% | 11.04 | 12.96 | 11.7 V | 12.7 V
[6 empty] | 12V | Aux1 8-pin (Note1) | -8% | 8% | 11.04 | 12.96 | 11.9 V | 12.9 V
[6 empty] | 12V | Aux2 8-pin (Note1) | -8% | 8% | 11.04 | 12.96 | NA | NA
Note 1: When two 8-pin aux cables are used instead of CPU-8-pin cable
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## Thermal
Thermal Qualification Data |  | Tesla M40 PCIe
IMPORTANT
If there may be multiple boards in this system chassis, thermal qualification must be performed on the worst-case board placement. Worst-case placement for thermal purposes is defined as placement that exhibits the highest GPU temperature and highest temperatures of other board components during the qualification run. Use this worksheet to report measurement results for the worst-thermal-case board placement. (Parameters relevant to worst thermal board placement can include minimum airflow rate through the card, air temperature at the board's inlet, presence or absence of other boards in system, other sources and conductance methods of thermal energy in the system, and other, as determined by thermal qualification.)
If minimizing the number of NVQual Thermal Qual runs is a priority, it may be useful to apply all thermocouples, airflow measurement devices, voltage probes, etc., before initiating an NVQual Thermal Qual run.
TEST CONFIGURATION
Environment for Cooling | Item | Description | Customer Results | Comments
| Card cooler type | Passive | Passive Cooler
| Card orientation wrt airflow | Left-to-right, Right-to-left, etc. | Leftt-to-Righ
| Airflow bypass at this card | % bypass
MODS Thermal Test | Item | Description | Customer Results | Comments
| Confirm thermocoupling of all critical components as identified by Thermal Map | Required to confirm. Enter "Waive" if Tinlet/CFM is within zone A (Figure 3-2 in SDG) | CONFIRMED
| How many MTT loops is run? | Required at least 3 loops for official qualification | CONFIRMED
| MODs Thermal Test Execution | Confirm PASS | PASS | Use of NVQual for thermal qual is mandatory, whether other workloads are also used or not. "PASS" is a requirement.
Other Thermal Qual Workload (Optional)) | Item | Description | Customer Results | Comments
| Name of Workload (App) | If customer has a preferred workload for thermal qual, please identify it here
| Workload/App Execution | Indicate PASS or FAIL |  | Use of secondary workloads for thermal qual is optional; thus "PASS" is optional and at the discretion of customer.
Air Measurements | Item | Description | Customer Results | Comments
| System external ambient temp (max) at chassis inlet | Customer’s max specified ambient temperature (outside system chassis) | 35 deg C
| Board inlet air temperature (max) during NVQual Thermal Qual execution | 35 - 45 deg C | 35 deg C
| Airflow measurement point | Select: Card inlet, card outlet | Card inlet
| CFM (min) | Measured airflow | 45 CFM
| System fan speed setting (% of maximum fan speed) | Describe PWM% setting OR percentage of maxium possible flow rate | Tested with all fans at 100% PWM. | example 1: Tested with all fan PWM% locked at 75% example 2: Tested with fans delivering 60% of maximum possible CFM example 3: Tested with all fans at 100% PWM.
GPU MEASUREMENTS
Gpu Tj (max) during NVQual Thermal Qual (must not exceed slow down temperature) | Qual App | Item | Specification | Customer Results (Tj) | Comments
| NVQual Thermal Qual | GPU 0 | 80C |  | Must see temp change in repeated system queries
Gpu Tj (max) during other qual run (must not exceed slow down temperature) | Qual App | Item | Specification | Customer Results (Tj) | Comments
| (List other qual application used, if any) | GPU 0 | 80C |  | Must see temp change in repeated system queries
COMPONENT MEASUREMENTS
Optional, only needed when Tinlet/CFM is not in Zone A
To locate components on board, see Assembly Drawing attached here:
Component Number on Thermal Map | Component Reference Designator (Critical; must monitor) * | Description | NVIDIA PART NUMBER | De-rated Max Tcase (C) | Customer Results (For NVQual Thermal Qual) | Customer Results (For other Qual App, if any)
2,3,4,5,6,7,8,9 | L1-L8 | NVVDD OUTPUT IND | 131-0397-000 | 120
10 | Q18-Q33 | NVVDD FET | 315-0705-000 | 100
15,16 | L9,L12 | FBVDD OUTPUT IND | 130-0614-000 | 100
17 | Q34-Q37 | FBVDD FET | 315-0705-000 | 100
18 | L25 | 12V INPUT IND | 131-0213-000 | 100
19 | U4 | 1V8 FET+DRIVER | 316-0348-000 | 120
20 | L19 | 1V8 OUTPUT IND | 131-0522-000 | 100
21 | U5 | PEX_DVDD FET+DRIVER | 316-0348-000 | 120
22 | L23 | PEX_DVDD OUTPUT IND | 131-0522-000 | 100
23 | L29 | 12V INPUT IND 8PIN | 131-0354-000 | 100
24 | L28 | 12V INPUT IND 6PIN | 131-0354-000 | 100
25 | C239,C241,C245,C246,C251,C253 OR C238,C240,C243,C248,C250,C255 | 12V INPUT CAP | 042-0072-000 or 041-0146-000 | 84
26 | U7 | 5V FET+DRIVER | 315-0829-000 | 120
27 | L26 | 5V IND | 131-0622-000 | 100
28 | U529-U536 | NVVDD DRIVER | 316-0375-000 | 116
29 | U524-U528 | NVVDDS DRIVER | 316-0375-000 | 116
30 | U540 | 2V5 LDO | 315-0615-000 | 120
See the SDG Thermal Qualification requirements to determine whether the critical components identified in the above table must be thermocoupled and monitored by the customer during thermal qualification. Customers should locate these components using the Assembly Drawing document attached as an icon above the table. NVIDIA monitors all the components flagged in the diagrams below when performing thermal qualification.
TOP SIDE:
BOTTOM SIDE:
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## Mechanical
Mechanical Qualification Data |  | Tesla M40 PCIe
| Item | Description | Customer Results | Comments Please add details regarding specific issues here.
| Type of System Chassis | Select chassis type | Other (specify in Comment field) | 3U chassis
| Number of identical cards in chassis | (specify) | 8
| Mechanical Fit Check | Confirm: Able to be installed and removed. | Confirmed
|  | Confirm: No interference when in place. | Confirmed
| Bracket | Present or Not Present | Bracket is Present
| Bracket mounting | M2.5 mounting screws (specify qty) |  | Asrockrack apply M3 thumb screw
|  | screw heads flush; | Confirmed
|  | Issues? | No
| Extender | Select extender type | No Extender
| Extender mounting | Confirm three M3 mounting screws installed
Confirm full screw travel
|  | Issues? | N/A
| Clearance around board (must be compliant with NVIDIA Form Factor AppNote) | Confirm no electrical or mechanical contact. | Confirmed
|  | Confirm compliance with NVIDIA Form Factor AppNote | Confirmed
|  | Confirm: Air path not obstructed at air inlet | Confirmed
| Power cable fit check | Confirm: Able to connect & disconnect. | Confirmed
|  | Confirm: No interference when in place. | Confirmed
|  | Confirm: No strain on connected cable | Confirmed
| I/O cable fit check | Confirm: Able to connect & disconnect. | Confirmed
|  | Confirm: No interference when in place. | Confirmed
|  | Confirm: No strain on connected cable | Confirmed
| Power Brake cable | Present or Not Present | Confirmed
| Power Brake cable fit check | Confirm: Able to connect & disconnect. | Confirmed
|  | Confirm: No interference when in place. | Confirmed
|  | Confirm: No strain on connected cable | Confirmed
| Heatsink | Confirm: No mechanical fit deformation. | Confirmed
|  | Confirm: No airflow alignment issues | Confirmed
| Shock and Vibration (if tested) | Indicate S&V Test Results | S&V Not Performed
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."
Tower chassis
Blade server (specify height in comment field: 1U, 2U, etc)
Other (specify in Comment field)
NVIDIA long offset extender
NVIDIA short offset extender
NVIDIA straight extender
Customer-provided extender
No Extender
Confirmed
Implemented
Not implemented
Bracket is Present
No Bracket
Power Brake Cable is Present
No Power Brake Cable
S&V PASSED
S&V FAILED
S&V Not Performed

## SMBus
System Management Data | Tesla M40 PCIe
Item | Customer Results | Comments
Are SMBus signals supplied to the card by the system PCIe slot? | Yes
Does the system's SMBus access the NVIDIA card (Direct), or does a BMC device control the bus that accesses the NVIDIA card(s)? | BMC device control the bus that accesses the NVIDIA card(s)
What is the DevID of the NVIDIA GPUs when reading via SMBus? | 0x15f8
Are accurate values seen when polling GPU Tj via SMBus when the card is idle or running a workload i.e. does the temperature values change as the card switches from an idle state to running a workload. | Yes
Does the system firmware support the SMBus Post Box interface (SMBPBI)? This support is required for any out-of-band access to the GPU (See DG-06034-002 for more information on the SMBPBI.) | Yes
Does the system firmware support NVIDIA Zero Power feature via SMBPBI? | No
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## PCI Express
PCIe Bus Qualification Data |  | Tesla M40 PCIe
| PCIe System Information | Customer Results | Comments
| Which PCIe gen is used (e.g. Gen3, Gen2, Gen1)? | Gen3
| Bus width of slot (e.g. x4, x8, x16) | x16
| Does the system use a PCIe riser card on the graphics card slot? | No
| Is the riser card active (e.g. uses a repeater) or passive? | NA
| Does the system use a PLX ROM? | Yes
| MODS PCIe Qual Test Note: Customers should provide the encrypted log file of each GPU in the system to NVIDIA for analysis. | Customer Results | Comments
| GPU 0: Pass/Fail? | Pass
| GPU 1: Pass/Fail? | Pass
| GPU 2: Pass/Fail? | Pass
| GPU 3: Pass/Fail? | Pass
| GPU 4: Pass/Fail? | Pass
| GPU 5: Pass/Fail? | Pass
| GPU 6: Pass/Fail? | Pass
| GPU 7: Pass/Fail? | Pass
| Bandwidth Test Note: Customers should record the bandwidth shown on the log file for each GPU in the system. This log file should be provided to NVIDIA. | Customer Results | Comments
GPU 0-7:
| Average Raw Bandwidth Obtained (Gen3) | As attachment
| Average Raw Bandwidth Obtained (Gen2) | As attachment
| Average Raw Bandwidth Obtained (Gen1) | As attachment
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## SBIOS Mapping
GPU Direct Test |  | Tesla M40 PCIe
BAR1 < 32bit
The GPU SBIOS mapping test is designed to verify the BAR1 mapping requirements for NVIDIA GRID and Tesla products. |  |  |  | 32bit < BAR1 < 42bit
For Tesla products supporting both graphics and compute mode, it is required to repeat this test in both modes. |  |  |  | BAR1 > 42bit
| SBIOS Mapping test Note: Customers should provide the log files to NVIDIA for analysis. | Customer Results | Comments
| Compute Mode (default) | 32bit < BAR1 < 42bit
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## Stress
Stress Test |  | Tesla M40 PCIe
Each loop runs for approximately 10 minutes
| MODS Stress Test (GLStress) Note: Customers should provide the log files to NVIDIA for analysis. | Customer Results | Comments
| Is stress test run for more than 12 hrs (60+ loops)? | Yes
| Does any GPU experience any thermal slow down? | No
| Does any GPU experience any power capping? | No
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## GPU Direct
GPU Direct Test |  | Tesla M40 PCIe
This test will measure GPU FB-to-GPU FB performance based on NVIDIA GPU Direct protocol. There is no PASS/FAIL criteria.
| MODS GPU Direct Test Note: Customers should provide the log files to NVIDIA for analysis. | Customer Results | Comments
| What is the GPU Direct Bandwidth result between the GPUs on different cards? Enter results for all possible GPU pairs as shown in the GPU Direct log file | Pass
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."

## Input EDPp
Input EDP |  | Tesla M40 PCIe
This test will generate peak current/power spike at the beginning of each loop and thus, can be used to test the system power supply if it can properly support the peak power as specified in the Board Spec
Each loop runs for approximately one hour.
Note:
1. The new Input EDPp test needs nvidia driver and CUDA SDK support, make sure to install nvidia driver and CUDA SDK correctly before running nvqual.
2. The new Input EDPp test will run for around one hour regardless of the loops setting.
| MODS Input EDP Test Note: Customers should provide the log files to NVIDIA for analysis. | Customer Results | Comments
| Does the system power supply shut down or cause a system reboot or crash? | Pass
Specifications in this worksheet are subject to change. Please check with NVIDIA to ensure you are using the latest values.
This entire Excel Workbook is "NVIDIA Confidential."