## Slide 1: ASRock Rack
ASRock Rack
16th June ‘16
1U2FH -4L TEST REPORT

## Slide 2: Content
System components
Thermal solution
Test situation
Test result
Conclusion

## Slide 3: Introduction
FAN1
FAN2
FAN3
FAN4
FAN5
HDD_1
HDD_2
CPU1
CPU2
DIMM1
DIMM16
HDD_3
HDD_4

## Slide 4: System components
Name | TDP (W) | Thermal Specification
Intel E5-2690 v3 | 135W | DTS max= 100℃
Memory DDR4 | 3.6W | Tc = 95℃
HDD | 10W | Tc = 55℃
Intel X540 | 12.5W | Tj = 110℃

## Slide 5: Thermal solution
Thermal Solution | Specification
System Fan | 
CPU H/S | 

## Slide 6: Test situation (25 °C)
Stress CPU tool: PTU
  CPU workload 100%
Stress HDD tool: IOmeter
  Random 100%, write 100%
Stress M540 card tool: Iperf
  Workload 90%~100%

## Slide 7: Test result-Stress tool use PTU, Iometer and IPerf
Fan | rpm
Fan1 | 16500rpm
Fan2 | 16600rpm
Fan3 | 16500rpm
Fan4 | 19000rpm
Fan5 | 18900rpm
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 77 | 100 | Pass
CPU2(Sensor) | 72 | 100 | Pass
Dimm(Tc. The highest) | 43 | 95 | Pass
HDD(Tc. The highest) | 29 | 55 | Pass
Intel X540 | 45 | 110 | Pass

## Slide 8: Test result-Stress tool use PTU and Iometer
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 78 | 100 | Pass
CPU2(Sensor) | 72 | 100 | Pass
Dimm(Tc. The highest) | 43 | 95 | Pass
HDD(Tc. The highest) | 28.9 | 55 | Pass
Intel X540 | 44 | 110 | Pass
Fan | rpm
Fan1 | 17800rpm
Fan2 | 17900rpm
Fan3 | 17900rpm
Fan4 | 20200rpm
Fan5 | 20200rpm

## Slide 9: Test result-Stress tool use Iometer
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 41 | 100 | Pass
CPU2(Sensor) | 37 | 100 | Pass
Dimm(Tc. The highest) | 32 | 95 | Pass
HDD(Tc. The highest) | 30.3 | 55 | Pass
Intel X540 | 56 | 110 | Pass
Fan | rpm
Fan1 | 7000rpm
Fan2 | 7100rpm
Fan3 | 7000rpm
Fan4 | 7000rpm
Fan5 | 7000rpm

## Slide 10: Test result-Stress tool use PTU
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 78 | 100 | Pass
CPU2(Sensor) | 72 | 100 | Pass
Dimm(Tc. The highest) | 42 | 95 | Pass
HDD(Tc. The highest) | 28.7 | 55 | Pass
Intel X540 | 44 | 110 | Pass
Fan | rpm
Fan1 | 17800rpm
Fan2 | 17900rpm
Fan3 | 17800rpm
Fan4 | 20200rpm
Fan5 | 20200rpm

## Slide 11: Test result-Stress tool use IPerf
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 51 | 100 | Pass
CPU2(Sensor) | 50 | 100 | Pass
Dimm(Tc. The highest) | 36 | 95 | Pass
HDD(Tc. The highest) | 30.1 | 55 | Pass
Intel X540 | 56 | 110 | Pass
Fan | rpm
Fan1 | 7000rpm
Fan2 | 7000rpm
Fan3 | 7000rpm
Fan4 | 7600rpm
Fan5 | 7800rpm

## Slide 12: Test result-Idel
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 41 | 100 | Pass
CPU2(Sensor) | 37 | 100 | Pass
Dimm(Tc. The highest) | 32 | 95 | Pass
HDD(Tc. The highest) | 30.8 | 55 | Pass
Intel X540 | 57 | 110 | Pass
Fan | rpm
Fan1 | 7000rpm
Fan2 | 7000rpm
Fan3 | 7000rpm
Fan4 | 7000rpm
Fan5 | 7000rpm

## Slide 13: Test situation(35 °C)
Stress CPU tool: PTU
  CPU workload 100%
Stress HDD tool: IOmeter
  Random 100%, write 100%
Stress M540 card tool: Iperf
  Workload 90%~100%

## Slide 14: Test result-Stress tool use PTU, Iometer and IPerf
Fan | rpm
Fan1 | 20200rpm
Fan2 | 20300rpm
Fan3 | 20300rpm
Fan4 | 21500rpm
Fan5 | 21600rpm
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 86 | 100 | Pass
CPU2(Sensor) | 80 | 100 | Pass
Dimm(Tc. The highest) | 52 | 95 | Pass
HDD(Tc. The highest) | 38.8 | 55 | Pass
Intel X540 | 55 | 110 | Pass

## Slide 15: Test result-Stress tool use PTU and Iometer
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 86 | 100 | Pass
CPU2(Sensor) | 80 | 100 | Pass
Dimm(Tc. The highest) | 52 | 95 | Pass
HDD(Tc. The highest) | 39.2 | 55 | Pass
Intel X540 | 54 | 110 | Pass
Fan | rpm
Fan1 | 20300rpm
Fan2 | 20300rpm
Fan3 | 20300rpm
Fan4 | 21500rpm
Fan5 | 21600rpm

## Slide 16: Test result-Stress tool use Iometer
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 50 | 100 | Pass
CPU2(Sensor) | 49 | 100 | Pass
Dimm(Tc. The highest) | 41 | 95 | Pass
HDD(Tc. The highest) | 39.8 | 55 | Pass
Intel X540 | 67 | 110 | Pass
Fan | rpm
Fan1 | 7000rpm
Fan2 | 7100rpm
Fan3 | 7100rpm
Fan4 | 7100rpm
Fan5 | 7000rpm

## Slide 17: Test result-Stress tool use PTU
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 86 | 100 | Pass
CPU2(Sensor) | 80 | 100 | Pass
Dimm(Tc. The highest) | 52 | 95 | Pass
HDD(Tc. The highest) | 38.6 | 55 | Pass
Intel X540 | 53 | 110 | Pass
Fan | rpm
Fan1 | 20300rpm
Fan2 | 20300rpm
Fan3 | 20300rpm
Fan4 | 21500rpm
Fan5 | 21600rpm

## Slide 18: Test result-Stress tool use IPerf
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 53 | 100 | Pass
CPU2(Sensor) | 51 | 100 | Pass
Dimm(Tc. The highest) | 43 | 95 | Pass
HDD(Tc. The highest) | 38.1 | 55 | Pass
Intel X540 | 57 | 110 | Pass
Fan | rpm
Fan1 | 13100rpm
Fan2 | 13100rpm
Fan3 | 13100rpm
Fan4 | 13100rpm
Fan5 | 13100rpm

## Slide 19: Test result-Idel
component temp(℃) | Test data | SPEC | Pass/fail
CPU1(Sensor) | 51 | 100 | Pass
CPU2(Sensor) | 49 | 100 | Pass
Dimm(Tc. The highest) | 40 | 95 | Pass
HDD(Tc. The highest) | 39.7 | 55 | Pass
Intel X540 | 67 | 110 | Pass
Fan | rpm
Fan1 | 7100rpm
Fan2 | 7100rpm
Fan3 | 7000rpm
Fan4 | 7100rpm
Fan5 | 7100rpm

## Slide 20: Conclusion
In Ta25℃ situation, key components in all test item are pass
In Ta35℃ situation, key components in all test item are pass