D1541D4I SNMP setting SOP

Preparation:

- SNMP detect tool: iReasoning

Download link http://www.ireasoning.com/download.shtml

(Just download MIB Browser Personal Edition)

2.	Host computer (receive SNMP trap)

3.	Client computer (D1541D4I, with BIOS P1.20 or later)

Steps

- Update your BMC version to D1540D4I_L0.21.00 first

- Login IPMI GUI  configuration  SNMP

- Set “ro” & “rw” to any value you want (Ex: we set the value as “123”) and save

- Find PEF setting (path: configuration PEF)

- Choose Event filter.

- Modify PEF ID.1 filter configuration as “Enable”

- Choose Alert policy

- Check if the policy number is set to “1” , and event specific must enable too.

- Choose Lan destination

- Input your Host IP address and save.

- Open iReasoning tool.

- Load your MIB file

- Input client’s IP address.

- Choose Advanced and set Read community (ro) and Write community (rw) the same value as step.3

- Check if the sensor value can be read by clicking those sensor items in MIB tree….

(It will show description and data on the right window)

- Open trap receiver

- Check Trap receiver function

IPMI GUIServer healthsensor readingchoose any sensor you want to test (For example: CPU tmp…)temporary set threshold to un-normal value (Ex: We set CPU tmp UNC to 40 Celsius)check if trap receiver can get warning message? After the check complete, please restore default sensor value

>>>Sensor reading page

>>>iReasoning receive SNMP trap (CPU temperature warning)